## Slide 1: EEE 333 Power System Analysis
Power System | Single Line Diagram | Per-Unit System
Prepared by
Mahzuba Islam
Sr. Lecturer, Dept. of EEE

## Slide 2
Lecture Contents
Power System Basics
Interconnected System and its Advantages
Single-Line or One-Line Diagram
Per-Unit System

## Slide 3
Learning Outcomes
The students will be able to
Learn the basic concepts of Power Supply Systems
Know how the interconnected system works
Get idea on one-line diagram
Understand the per-unit system

## Slide 4
Brief History of Electric Power
First real practical uses of electricity began with the telegraph (1860's) and then arc lighting in the 1870’s
Early 1880’s – Edison introduced Pearl Street dc system in Manhattan supplying 59 customers
1884 – Sprague produces practical dc motor
1885 – invention of transformer
Mid 1880’s – Westinghouse/Tesla introduce rival ac system
Late 1880’s – Tesla invents ac induction motor
1893 – Three-phase transmission line at 2.3 kV
1896 – ac lines deliver electricity from hydro generation at Niagara Falls to Buffalo, 20 miles away; also 30kV line in Germany

## Slide 5
Brief History of Electric Power
Early 1900’s – Private utilities supply all customers in area (city); recognized as a natural monopoly; states step in to begin regulation
By 1920’s – Large interstate holding companies control most electricity systems
1935 – Congress passes Public Utility Holding Company Act to establish national regulation, breaking up large interstate utilities (repealed 2005)
    This gave rise to electric utilities that only operated in one state
1935/6 – Rural Electrification Act brought electricity to rural areas
1930’s – Electric utilities established as vertical monopolies
Frequency standardized in the 1930’s
1970’s brought inflation, increased fossil-fuel prices, calls for conservation and growing environmental concerns

## Slide 6
Power System Basics
All power systems have three major components:
  Generation, Transmission/Distribution and Load
Generation: Creates electric power
Transmission/Distribution: Moves electric power from generation to load.
  Lines/transformers operating at voltages above 100 kV are usually called the Transmission system. The transmission system is usually networked.
  Lines/transformers operating at voltages below 100 kV are usually called the Distribution system. The distribution system is usually radial except in urban areas.
Load: Consumes the power, final destination

## Slide 7
Power System Basics

## Slide 8
Power System
Power system analysis is a branch of electrical engineering for designing entire power systems consisting of generators, transformers, capacitor banks, shunt reactances, transmission lines and so on.
This is different from electrical installation design for consumer premises in that the latter not only pertains to low voltage but also assume availability of a stable power supply from utility, while power system analysis is concerned with designing the utility itself.

## Slide 9
Interconnected System
The connection of several generating station in parallel is known as interconnected system.
Advantages
Exchange of peak loads
Use of older power plants
Ensures economical operations
Increases diversity factor
Reduces plant reserve capacity
Increases reliability of supply

## Slide 10
Several Advantages
Exchange of peak loads. An important advantage of interconnected system is that the peak load of the power station can be exchanged. If the load curve of a power station shows a peak demand that is greater than the rated capacity of the plant, then the excess load can be shared by other stations interconnected with it.
Use of older power plants. The interconnected system makes it possible to use the older and less efficient plants to carry peak loads of short durations. Although such plants may be inadequate when used alone, yet they have sufficient capacity to carry short peaks of loads when interconnected with other modern plants. Therefore, interconnected system gives a direct key to the use of obsolete plants.
Ensure economical operation. The interconnected system makes the operation of concerned power stations quite economical. It is because sharing of load among the stations is arranged in such a way that more efficient stations work continuously through outs the year at a high load factor and the less efficient plants work for peak load hours only.
Increases diversity factor. The load curves of different interconnected stations are generally different. The result is that the maximum demand on the system is much reduced as compared to the sum of individual maximum demands on different stations. In other words, the diversity factor of the system is improved, thereby increasing the effective capacity of the system.

## Slide 11
Several Advantages
Reduces plant reserve capacity Every power station is required to have a standby unit for emergencies. However, when several power stations are connected in parallel, the reserve capacity of the system is much reduced. This increases the efficiency of the system.
Increases reliability of supply. The interconnected system increases the reliability of supply. If a major breakdown occurs in one station, continuity of supply can be maintained by other healthy stations.

## Slide 12
One-Line / Single-Line Diagram
A one-line diagram or single-line diagram (SLD) is a simplified notation for representing a three-phase power system.
The one-line diagram has its largest application in power flow studies. Electrical elements such as circuit breakers, transformers, capacitors, bus bars, and conductors are shown by standardized schematic symbols. Instead of representing each of three phases with a separate line or terminal, only one conductor is represented. It is a form of block diagram graphically depicting the paths for power flow between entities of the system. Elements on the diagram do not represent the physical size or location of the electrical equipment, but it is a common convention to organize the diagram with the same left-to-right, top-to-bottom sequence as the switchgear or other apparatus represented.

## Slide 13
Per-Unit System
It is usual to express voltage, current, voltamperes and impedance of an electrical circuit in per unit (or percentage) of base or reference values of these quantities. The Per Unit System Definition value of any quantity is defined as:
The Per Unit System is particularly convenient in power systems as the various sections of a power system are connected through transformers and have different voltage levels which converted to single voltage level. In this system, the different voltage levels disappear and a power network involving generators, transformers and lines (of different voltage levels) reduces to a system of simple impedance.

## Slide 14
Advantages of Per-Unit System
The per-unit system gives a clear idea of relative magnitudes of various quantities such as voltage, current, power and impedance
The per-unit impedance of equipment of the same general type based on their own ratings fall in a narrow range regardless of the rating of the equipment. Whereas their impedance in ohms vary greatly with the rating
The per-unit values of impedance, voltage and current of a transformer are the same regardless of whether they are referred to the primary or the secondary side. This a great advantage since the different voltage levels disappear and the entire system reduces to a system of simple impedance
The per-unit systems are ideal for the computerized analysis and simulation of complex power system problems
The circuit laws are valid in per-unit systems and the power and voltage equations are simplified since the factor of 3 ad 3 are eliminated in the per-unit system

## Slide 15
Formulation - Per-Unit System

## Slide 16
Formulation - Per-Unit System

## Slide 17
Formulation - Per-Unit System

## Slide 18
Change of Base
The impedance of individual generators and transformers, as supplied by the manufacturer, are generally in terms of percent or per-unit quantities based on their own ratings. The impedance of transmission lines are usually express in per-unit on a common system base. To accomplish this, an arbitrary base for apparent power is selected and then the voltage bases must be selected. Once a voltage base has been selected for a point in a system, the remaining voltage bases are no longer independent; they are determined by the various transformer turns ratios.

## Slide 19
Change of Base

## Slide 20
3- Per-unit Conversion Procedure
Pick a 3 VA base for the entire system
Pick a voltage base for each different voltage level, VB. Voltages are line to line.
Calculate the impedance base
Use a 3 VA base, and use line to line voltage bases
Calculate the current base, IB
Convert actual values to per unit quantities